## Consumption
Project | HOUSING |  |  | Location | POLAND
Engineer | VIPSKILLS |  |  | Date | 2017-07-04
CALCULATION OF YEARLY AVERAGE CONSUMPTION
LOAD DESCRIPTION | Nº of Loads | Current (A) | Voltage (V) | AC Power (W) | Daily cycle (hours/day) | Week cycle (days/week) | Efficiency of converssion | Nominal voltage (V) | Consumtion Amp-Hour (Ah/day)
AC LOADS
WATER PUMP | 1 | 4 | 220 | 880 | 2 | 7 | 0.88 | 220 | 9.0909
FRIDGE | 1 | 2 | 220 | 440 | 24 | 7 | 0.9 | 220 | 53.3333
OVEN | 1 | 5 | 220 | 1100 | 0.5 | 2 | 0.8 | 220 | 0.89286
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
CARGAS EN DC
INSIDE LIGHTING | 25 | 0.5 | 24 | 300 | 6 | 7 | 0.8 | 24 | 93.75
OUTSIDE LIGHTING | 5 | 0.7 | 24 | 84 | 8 | 7 | 0.8 | 24 | 35
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  | Total Power (W) | 2804 |  |  |  | Total Consumption (Ah/day) | 192.0671
| Total DC Power (W) | Total AC Power (W) | Nominal voltage (V) | Peak current (A) | Total consumption Ah/day | Wiring Efficiency factor | Battery efficiency factor de la batería | Reviewed Total Consumption (Ah/día)
| 384 | 2420 | 220 | 12.7455 | 192.0671 | 0.98 | 0.95 | 206.3019
Note on J10: inversor dc/ac 0,8 converter dc/dc 0,85

## Inclination angle
| Project |  | HOUSING | [7 empty] | Location | POLAND
| Engineer |  | VIPSKILLS | [7 empty] | Date | 2017-07-04
INTENSITY AND INCLINATION ANGLE | [10 empty] | Location | Madrid | Latitud | -33
1
|  |  |  | Inclination angle | 19
| Month | Reviewed total consumption | Total daily consumption Ah/day | Solar Peak Hours per day | Design current (A) |  |  |  |  | Year Optimal angle |  | 26.47 | Winter optimal angle |  | 13
| January |  | 206.3019 | 5.4182 | 38.0754 | 0 | 5.4182 | January | 167.9655 | Peak sun hours (hrs/día) | Design current (A) | Month | Peak sun hours (hrs/day) | Design current (A) | Month
| February |  | 206.3019 | 5.2241 | 39.4901 | 0 | 5.2241 | February | 146.2761 | 3.5283 | 58.4706 | March | 3.9671 | 52.0032 | Marzo
| March |  | 206.3019 | 3.7864 | 54.4851 | 0 | 3.7864 | March | 117.3781
| April | 35 | 206.3019 | 2.4674 | 83.6117 | 35 | 2.4674 | April | 74.0215 | Summer optimal angle |  | 18 | Selected angle |  | 19
| May | 56 | 206.3019 | 1.5605 | 132.2059 | 56 | 1.5605 | May | 48.3742 | Peak sun hours (hrs/day) | Design current (A) | Month | Peak sun hours (hrs/day) | Design current (A) | Month
| June | 58 | 206.3019 | 1.2569 | 164.135 | 58 | 1.2569 | June | 37.7071 | 5.6917 | 36.2462 | November | 6.0986 | 33.8277 | December
| July | 32 | 206.3019 | 1.4226 | 145.0183 | 32 | 1.4226 | July | 44.1004
| August | 45 | 206.3019 | 2.1208 | 97.2748 | 45 | 2.1208 | August | 65.7453
| September | 48 | 206.3019 | 3.2686 | 63.1165 | 48 | 3.2686 | September | 98.0577
| October |  | 206.3019 | 4.0156 | 51.3747 | 0 | 4.0156 | October | 124.4846 | [6 empty] | Ángulo inclinación |  |  | 26.47 |  |  |  | Ángulo inclinación |  |  | 18 |  |  |  | Ángulo inclinación |  |  | 13
| November |  | 206.3019 | 5.6707 | 36.3804 | 0 | 5.6707 | November | 170.1206 | [6 empty] | Mes | Consumo Corregido (Ah/día) | Consumo Corregido (Ah/día) | Horas sol pico día | Intensidad de diseño (A) |  |  | Mes | Consumo Corregido (Ah/día) | Consumo Corregido (Ah/día) | Horas sol pico día | Intensidad de diseño (A) |  |  | Mes | Consumo Corregido (Ah/día) | Consumo Corregido (Ah/día) | Horas sol pico día | Intensidad de diseño (A)
| December |  | 206.3019 | 6.0986 | 33.8277 | 0 | 6.0986 | December | 189.057 | [6 empty] | January | 0 | 206.3019 | 5.8562 | 35.2277 | 5.8562 | January | January | 0 | 206.3019 | 6.0567 | 34.062 | 6.0567 | January | January | 0 | 206.3019 | 6.1354 | 33.6247 | 6.1354 | Enero
| TOTAL SOLAR PEAK HOURS: |  |  | 42.3105 | [11 empty] | February | 0 | 206.3019 | 5.2318 | 39.4324 | 5.2318 | February | February | 0 | 206.3019 | 5.5095 | 37.4446 | 5.5095 | February | February | 0 | 206.3019 | 5.0935 | 40.5026 | 5.0935 | Febrero
[16 empty] | March | 0 | 206.3019 | 3.5283 | 58.4706 | 3.5283 | March | March | 0 | 206.3019 | 3.8182 | 54.0309 | 3.8182 | March | March | 0 | 206.3019 | 3.9671 | 52.0032 | 3.9671 | Marzo
[16 empty] | November | 0 | 206.3019 | 5.4803 | 37.6445 | 5.4803 | November | November | 0 | 206.3019 | 5.6917 | 36.2462 | 5.6917 | November | November | 0 | 206.3019 | 5.7803 | 35.6903 | 5.7803 | Noviembre
[16 empty] | December | 0 | 206.3019 | 5.941 | 34.7253 | 5.941 | December | December | 0 | 206.3019 | 6.1147 | 33.7384 | 6.1147 | December | December | 0 | 206.3019 | 6.1774 | 33.396 | 6.1774 | Diciembre
[16 empty] | HORAS SOL PICO TOTALES: |  |  | 26.0376 |  |  |  | HORAS SOL PICO TOTALES: |  |  | 27.1908 |  |  |  | HORAS SOL PICO TOTALES: |  |  | 27.1538

## Battery
|  | Project | HOUSING |  |  |  | Location | POLAND
|  | Engineer | VIPSKILLS |  |  |  | Date | 2017-07-04
BATTERY ANALISYS
|  | INFORMATION OF BATTERY |  |  |  | WARNINGS
|  | Manufacturer |  |  |  | INCREASE OF BATTERIES CAPACITY IS RECOMENDED |  |  | 7 | 10
|  | Model |  |  |  | INCREASE OF BATTERIES CAPACITY IS RECOMENDED
|  | Type |  |  |  | IMPROPER NUMBER OF BATTERIES
|  | Nominal Voltage | 12
Floating voltage 25º C (V)
Equalization voltage 25ºC (V)
|  | C100 (Ah) | 108
Total Consumption Ah reviewed (Ah/day) | Month | Nº of days of autonomy | Max Discharge Deepth | Correction for temperature | Needed capacity of batteries (Ah) | Capacity of selected battery (Ah) | Recomended parallel batteries | Selected parallel batteries
206.3019 | December | 3 | 0.7 | 1 | FALSE | 108 | 0 | 1 |  |  |  | 1.618 | 33.8277
|  |  | Nominal voltage (V) | Battery nominal voltage (V) | Serial batteries | Parallel batteries | Nº of batteries
|  |  | 220 | 12 | 18.3333 | 1 | 18.3333
Batteries in parallel | Capacity of batteries C100(Ah) | Capacity of batteries system (Ah) | Stational discharge deepth factor | Useful capacity (Ah) | Real Daily average discharge deepth (%) | Average deepth of discharge at the end of autonomy (%) | Recovery period in Winter 100% of battery load (days) | Recuperation period in summer 100% batteries load (days)
1 | 108 | 108 | 0.7 | 75.6 | 143.3% | 716.3% | DEGRADATION OF BATTERIES | DEGRADATION OF BATTERIES |  |  | -1 | DEGRADATION OF BATTERIES | 0 | DEGRADATION OF BATTERIES
Note on F19: waliki: Tipo de batería Valor defecto plomo antimonio 0,8 plomo calcio 0,6 niquel cadmio 0,9

## PV
| Project | HOUSING |  |  |  | Location | POLAND
| Engineer | VIPSKILLS |  |  |  | Date | 2017-07-04
PV GENERATORS
INFORMATION OF PV MODULE
Manufacturer and Model
Tipe
| Power (Wp) | 70
| Vmp (V) | 17.4 | Voc (V) | 21.7
| Imp (A) | 4.14 | Isc (A) | 5.01
| Reviewed current (A) | Factor de corrección del módulo | Design current | Module nominal current (A) | Recomended parallel modules | Recomended serial modules | Selecteed parallel modules | Selected serial modules | Peak power per module (Wp)
| 33.8277 | 0.95 | 35.6081 | 4.14 | 9 | 13 | 1 | 1 | 70
Nominal voltage (V) | Module Nominal voltage (V) | Modules in parallel | Modules in serial | Total Modules | Nominal voltage (V) | Floating max voltage (V) | Equalization max voltage | Max environment temp ºC | Cell tremperature ºC |  | Open circuit at Tc (V) | 75.6 | 6.0986 | #REF! | #REF! | 33.8277 | #REF!
220 | 12 | 1 | 1 | 1 | 21.7 | 0 | 0 | 20 | 50.375 | 2.7532 | 18.9468 |  | #REF!

## Load Reg.
| Project | HOUSING |  |  | Location | POLAND
| Engineer | VIPSKILLS |  |  | Date | 2017-07-04
CHARGE REGULATOR
| INFORMATION OF CHARGE REGULATOR |  |  |  | WARNINGS
| Model | SOLARTEC RC |  |  | wrong selected voltage
| Tipe | RC48-N |  |  |  |  | 1
| Voltaje (V) | 48 |  |  |  |  | 1
| ADJUSTED SWICH POINTS | [5 empty] | 1
| Compensation of temperature |  |  | Y |  |  | 1
| Overload voltage limit |  |  | Y |  |  | 0
| Overdischarge voltage limit |  |  | Y
| Overdischarge voltage rearmament |  |  | Y
| track MPP |  |  | Y
| Inverse current protection |  |  | Y
Needs of the system
| Voltage (V) |  |  | 24
| Current (A) |  |  | 6.2625
| Load DC Current (A) |  |  | 128.75
| Isc generator (A) | Min Current regulator (A) | Nominal current regulator (A) | Regulators in parallel
| 5.01 | 6.2625 | 60 | 1

## Power acond
Project | HOUSING |  | Location | POLAND
Engineer | VIPSKILLS |  | Date | 42920
POWER ANALISYS
INVERSOR
REQUIREMENTS |  | INVERTERS SPECIFICATIONS
Wave form | 1 | Manufacturer | Victron |  |  |  | SENOIDAL PURA | 6 | 120 | SI | 21.6
Voltage DC (V) | 4 | Model | 48/5000/70 |  |  |  | MODIFICADA | 12 | 130 | NO | 140
Voltage AC (V) | 3 | Wave form | SENOIDAL PURA |  |  |  | CUADRADA | 24 | 220
Max power (W) |  | Voltage (DC) | 48 | (V) |  |  |  | 48 | 230
simultaneity coefficent (%) | 75 | Voltage (AC) | 230 | (V) |  |  |  | 120
Min nominal power (W) | 0 | Nominal power (W) | 4250 |  | Nº of inverters selected | Total AC power (W) |  | 240
overload operation time (min.) |  | Peak max power (W) | 10000 | (W)
efficiency in nominal load (%) | 0.9 | Nº inverters MIN. Needed | 0 |  | 2 | 8500
|  | Inverter-Charger | 1
|  | Input voltage (V) | 230
|  | Max load current (A) | 70
|  | Batteries Time of charge (h) | 0.54
|  | Compensation of voltage | 1
|  | Sensor of Tª | 1
|  | Atomatic commutation system | 1
DIESEL GENERATOR
Characteristics:
Model
Nominal power (W)
Max power (W)
Voltage (V)
Fuel type
Autonomy
Start system
DC/DC converter
REQUIREMENTS |  | Specifications converter DC/DC
DC Input voltage (V) |  | Manufacturer
DC output voltage (V) |  | Model
Output power (W) |  | Input voltage (V)
temperature of operation (ºC) |  | Output voltage (V)
output current (A)
Operation temperature (ºC)
Characteristics:
Output variable voltage
Note on D11: David Bullejos: 1: senoidal 2: modified 3: square
Note on D12: David Bullejos: 1:24 2:48 3:120 4:240
Note on D13: David Bullejos: 1:120 2:130 3:220 4:230

## Protection
Project | HOUSING |  |  |  |  | Location | POLAND
Engineer | VIPSKILLS |  |  |  |  | Date | 2017-07-04
PROTECTION COMPONENTS
Generator-Regulator | [7 empty] | 1
PV generator Isc (A) | Generator max current (A) | generator Voc (V) |  | Interruptor | Fuse | Comercial Interruptor | Comercial fuse
5.01 | 6.2625 | 21.7 | Max current (A) | 7.8281 | 7.8281
|  |  | Max voltage (V) | 21.7 | 21.7
Tipe
Regulator- DC Consumption
Peak DC current (A) | Max DC current (A) | Max DC voltage (V) |  | Interruptor | Fuse | Comercial Interruptor | Comercial fuse
1.7455 | 2.1818 | 220 | Max current (A) | 2.7273 | 2.7273
|  | 220 | Max voltage (V) | 220 | 220
|  | 220 | Tipe
Battery-Inverter
Inverter nominal power (W) | Efficiency | DC max voltage (V) |  | Interruptor | Fuse | Comercial Interruptor | Comercial fuse
4250 | 0.9 | 48 | Nominal current (A) | 122.9745 | 122.9745
|  |  | Nominal voltage (V) | 48 | 48
Tipe
Inverter- AC consumption
Intensidad máxima AC (A) | Intensidad máxima AC corregida | Tensión máxima AC (V) |  | Thermal Interruptor | Diferential Interruptor | Thermal Comertial | Diferential Comertial
5.2609 | 6.5761 | 230 | Nominal current (A) | 8.2201 | 8.2201
|  |  | Nominal voltage (V) | 230 | 230
Tipe
Other interruptors
Max current (A) | Reviewed max current (A) | Max voltage (V) |  | Interruptor | Fuse | Comercial Interruptor | Comercial fuse
| 0 |  | Nominal current (A) | 0 | 0 | 19
|  |  | Nominal voltage (V) | 0 | 0 | 24
Tipe
| 0 |  | Nominal current (A) | 0 | 0
|  |  | Nominal voltage (V) | 0 | 0
Tipe
| 0 |  | Nominal current (A) | 0 | 0
|  |  | Nominal voltage (V) | 0 | 0
Tipe
| 0 |  | Nominal current (A) | 0 | 0
|  |  | Nominal voltage (V) | 0 | 0
Tipe

## Wiring
Project | HOUSING |  |  |  |  | Location | POLAND
Engineer | VIPSKILLS |  |  |  |  | Date | 42920
SYSTEM WIRING
Conductors | Voltage (V) | Max current (A) | Length (m) | Voltage decrease (%) | Section mm2 | Comercial section mm2 | comercial voltage decrease (%) | Imax (A) | Temp correction | nº conductors | Reviewed Imax (A) | Pretection systems | Comercial section
DC SYSTEMS
Generator to regulator | 220 | 6.2625 | 8 | 1.5 | 0.54047 | 10 | 0.081071 | 49 | 1 | 1 | 49 | correct section | correct section
Regulador a consumo DC | 220 | 2.1818 |  |  |  |  | 0 |  |  |  | 0 | sección correcta | sección incorrecta
Battery to inverter | 220 | 208.3333 | 2 | 1.5 | 4.4949 | 50 | 0.13485 | 130 | 1 | 1 | 130 | correct section | no correct section
Regulator to battery | 220 | 6.012 | 6 | 1.5 | 0.38914 | 10 | 0.058371 | 49 | 1 | 1 | 49 | correct section | correct section
AC SYSTEMS
Inverter to AC load | 230 | 6.5761 | 50 | 2 | 2.5447 | 10 | 0.50893 | 50 | 1 | 1 | 50 | correct section | correct section
OTHER CIRCUITS
[7 empty] | 1 |  |  |  | 0 | no correct section | no correct section
[11 empty] | 0 | correct section | no correct section
[11 empty] | 0 | correct section | no correct section
[11 empty] | 0 | correct section | no correct section
ground of equipments | Section |  |  |  | Ground type
ground of system
Note on G9: waliki: Se recomienda que en cualquier tramo de la instalación las caídas de tensión sean inferiores al 1,5%
Note on L9: waliki: Si el cable va a trabajar a más de 40ºC consultar tabla 7 ITC_BT_06
Note on M9: waliki: Si va a haber más de un conductor, consultar Tabla 6 ITC_BT_06

## Hybrids
| Project | HOUSING | [5 empty] | Location | POLAND
| Engineer | VIPSKILLS | [5 empty] | Date | 2017-07-04
HYBRID PV-WIND SYSTEM
| Rotor heigh |  | 30 |  |  | Less PV |  | June |  |  |  | FALSE
| Aerogenerator efficiency |  | 0.19 |  |  | Worse wind month |  | December |  |  |  | FALSE |  |  | 1.2569 | 6 | 19 | 51726.5868
| Cost R fv (€/kWp) |  | 4450 | [8 empty] | FALSE |  |  | 2.5 | 12 |  | 58770.3342
| Cost R wind (€/m2) |  | 400 | [6 empty] | Cost (Euros) | [7 empty] | 61997.9008
[6 empty] | Only PV configuration (kWp) |  | 36.1097 |  | 160688.1737 | [7 empty] | 69545.0175
[6 empty] | Onli wind configuration (m2) |  | 397.7963 |  | 159118.5334
[6 empty] | Hybrid optimal configuration | FV (Kwp) | 7.6116 |  | 62071.9041
[7 empty] | (m2) | 70.5013
[6 empty] | 2nd best Hybrid configuration | FV (Kwp) | 7.1123 |  | 70524.401
[7 empty] | (m2) | 97.1865
[6 empty] | 3rd best Hybrid configuration | FV (Kwp) | 11.8219 |  | 74397.481
[7 empty] | (m2) | 54.4754
[6 empty] | 4th best Hybrid configuration | FV (Kwp) | 10.699 |  | 83454.021
[7 empty] | (m2) | 89.6087
| Month | Peak sun hours | Wind speed (m/s) | Wind speed at rotor (m/s) | Densidad de potencia | Energy density Wind x Effi | Daily consumption(kWh/day) | PV generated energy (kWh/day) |  | Wind generated energy (kWh/day) | Hybrid optimal generated energy (kWh/day) | Hybrid 2nd best generated energy (kWh/day) | Hybrid 3rd best generated energy (kWh/day) | Hybrid 4th best generated energy (kWh/day) | f | e |  | m | n | n1 | m1 | n1-m1 | n-m | A(m2) | P(kWp) | Condicionantes Área | Condicionantes Potencia |  | Min Área | Máxima P | Comprobación P |  |  |  | Coste
1 | January | 5.4182 | 3 | 3.5098 | 1.0377 | 0.19716 | 45.3864 | 195.6511 |  | 78.4277 | 55.1409 | 57.6971 | 74.7939 | 75.6366 | 8.3766 | 230.2062 | Enero-Febrero | 0.036387 | 0.03409 | 8.6878 | 8.3766 | 0.31122 | -0.0022976 | -135.4527 | 13.3054 | 0 | 13.3054 |  | 45.9239 | 32.4251 | 6.7055 | fallo
2 | February | 5.2241 | 2.9 | 3.3928 | 0.93732 | 0.17809 | 45.3864 | 188.6424 |  | 70.8435 | 52.3194 | 54.4637 | 71.4607 | 71.8515 | 8.6878 | 254.8513 | Enero-Marzo | 0.036387 | 0.047034 | 11.9867 | 8.3766 | 3.6101 | 0.010647 | 339.0798 | -3.9616 | 339.0798 | 0 | 339.0798
3 | March | 3.7864 | 2.9 | 3.3928 | 0.93732 | 0.17809 | 45.3864 | 136.7254 |  | 70.8435 | 41.3759 | 44.2379 | 54.4637 | 56.469 | 11.9867 | 254.8513 | Enero-Abril | 0.036387 | 0.1499 | 18.3946 | 8.3766 | 10.018 | 0.11352 | 88.2509 | 5.1654 | 88.2509 | 5.1654 | 88.2509
4 | April | 2.4674 | 3.7 | 4.3287 | 1.9467 | 0.36987 | 45.3864 | 89.0964 |  | 147.1334 | 44.857 | 53.4953 | 49.3179 | 59.5422 | 18.3946 | 122.7088 | Enero-Mayo | 0.036387 | 0.15334 | 29.0853 | 8.3766 | 20.7087 | 0.11695 | 177.076 | 1.9333 | 177.076 | 1.9333 | 177.076
5 | May | 1.5605 | 3.2 | 3.7438 | 1.2593 | 0.23927 | 45.3864 | 56.3477 |  | 95.1822 | 28.7466 | 34.3527 | 31.4821 | 38.1364 | 29.0853 | 189.6841 | Enero-Junio | 0.036387 | 0.22834 | 36.1097 | 8.3766 | 27.7331 | 0.19195 | 144.4797 | 3.1194 | 144.4797 | 3.1194 | 144.4797
6 | June | 1.2569 | 3.4 | 3.9778 | 1.5105 | 0.287 | 45.3864 | 45.3864 |  | 114.1676 | 29.8009 | 36.832 | 30.4934 | 39.1653 | 36.1097 | 158.1408 | Enero-Julio | 0.036387 | 0.18446 | 31.904 | 8.3766 | 23.5274 | 0.14807 | 158.8892 | 2.595 | 158.8892 | 2.595 | 158.8892
7 | July | 1.4226 | 3.3 | 3.8608 | 1.3811 | 0.26241 | 45.3864 | 51.3694 |  | 104.3873 | 29.3287 | 35.621 | 31.1128 | 38.7349 | 31.904 | 172.9573 | Enero-Agosto | 0.036387 | 0.092962 | 21.4005 | 8.3766 | 13.0239 | 0.056575 | 230.2062 | 0 | 230.2062 | 0 | 230.2062
8 | August | 2.1208 | 3 | 3.5098 | 1.0377 | 0.19716 | 45.3864 | 76.582 |  | 78.4277 | 30.0424 | 34.2448 | 35.8121 | 40.3574 | 21.4005 | 230.2062 | Enero-Septiembre | 0.036387 | 0.066553 | 13.8856 | 8.3766 | 5.509 | 0.030166 | 182.624 | 1.7314 | 182.624 | 1.7314 | 182.624
9 | September | 3.2686 | 3.1 | 3.6268 | 1.1449 | 0.21754 | 45.3864 | 118.0278 |  | 86.5348 | 40.2156 | 44.3888 | 50.4912 | 54.4637 | 13.8856 | 208.6391 | Enero-Octubre | 0.036387 | 0.03196 | 11.3024 | 8.3766 | 2.9258 | -0.004427 | -660.9018 | 32.4251 | 0 | 32.4251
10 | Ocober | 4.0156 | 2.6 | 3.0418 | 0.67548 | 0.12834 | 45.3864 | 145.0033 |  | 51.0536 | 39.6134 | 41.0335 | 54.4637 | 54.4637 | 11.3024 | 353.6395 | Enero-Noviembre | 0.036387 | 0.028267 | 8.0037 | 8.3766 | -0.37291 | -0.0081201 | 45.9239 | 6.7055 | 45.9239 | 6.7055 | 45.9239
11 | November | 5.6707 | 2.8 | 3.2758 | 0.84366 | 0.16029 | 45.3864 | 204.7669 |  | 63.7647 | 54.4637 | 55.9102 | 75.7702 | 75.0345 | 8.0037 | 283.1436 | Enero-Diciembre | 0.036387 | 0.018708 | 7.4421 | 8.3766 | -0.93451 | -0.017679 | 52.8595 | 6.4532 | 52.8595 | 6.4532 | 52.8595
12 | December | 6.0986 | 2.5 | 2.9248 | 0.6005 | 0.11409 | 45.3864 | 220.2191 |  | 45.3864 | 54.4637 | 54.4637 | 78.3123 | 75.4729 | 7.4421 | 397.7963 | Febrero-Marzo | 0.03409 | 0.047034 | 11.9867 | 8.6878 | 3.2989 | 0.012944 | 254.8513 | 0 | 254.8513 | 0 | 254.8513 | 80.9887 | 5.9269 | 5.9269 | ok | 80.9887 | 5.9269 | 58770.3342 | 80.9887 | 5.9269
[17 empty] | Febrero-Abril | 0.03409 | 0.1499 | 18.3946 | 8.6878 | 9.7068 | 0.11581 | 83.8129 | 5.8307 | 83.8129 | 5.8307 | 83.8129
[17 empty] | Febrero-Mayo | 0.03409 | 0.15334 | 29.0853 | 8.6878 | 20.3975 | 0.11925 | 171.0542 | 2.8566 | 171.0542 | 2.8566 | 171.0542
[17 empty] | Febrero-Junio | 0.03409 | 0.22834 | 36.1097 | 8.6878 | 27.4219 | 0.19425 | 141.1686 | 3.8754 | 141.1686 | 3.8754 | 141.1686
[17 empty] | Febrero-Julio | 0.03409 | 0.18446 | 31.904 | 8.6878 | 23.2162 | 0.15037 | 154.3918 | 3.4246 | 154.3918 | 3.4246 | 154.3918
[17 empty] | Febrero-Agosto | 0.03409 | 0.092962 | 21.4005 | 8.6878 | 12.7126 | 0.058872 | 215.9356 | 1.3266 | 215.9356 | 1.3266 | 215.9356
[17 empty] | Febrero-Septiembre | 0.03409 | 0.066553 | 13.8856 | 8.6878 | 5.1978 | 0.032464 | 160.1121 | 3.2296 | 160.1121 | 3.2296 | 160.1121
[17 empty] | Febrero-Octubre | 0.03409 | 0.03196 | 11.3024 | 8.6878 | 2.6146 | -0.0021294 | -1227.8545 | 50.5451 | 0 | 0
[17 empty] | Febrero-Noviembre | 0.03409 | 0.028267 | 8.0037 | 8.6878 | -0.68413 | -0.0058225 | 117.497 | 4.6824 | 117.497 | 4.6824 | 117.497
[17 empty] | Febrero-Diciembre | 0.03409 | 0.018708 | 7.4421 | 8.6878 | -1.2457 | -0.015381 | 80.9887 | 5.9269 | 80.9887 | 5.9269 | 80.9887
[17 empty] | Marzo-Abril | 0.047034 | 0.1499 | 18.3946 | 11.9867 | 6.4078 | 0.10287 | 62.2906 | 9.0569 | 62.2906 | 9.0569 | 62.2906 | 45.3962 | 9.8516 | 9.8516 | ok | 45.3962 | 9.8516 | 61997.9008 | 45.3962 | 9.8516
[17 empty] | Marzo-Mayo | 0.047034 | 0.15334 | 29.0853 | 11.9867 | 17.0986 | 0.1063 | 160.8501 | 4.4213 | 160.8501 | 4.4213 | 160.8501
[17 empty] | Marzo-Junio | 0.047034 | 0.22834 | 36.1097 | 11.9867 | 24.123 | 0.1813 | 133.0521 | 5.7287 | 133.0521 | 5.7287 | 133.0521
[17 empty] | Marzo-Julio | 0.047034 | 0.18446 | 31.904 | 11.9867 | 19.9173 | 0.13743 | 144.9294 | 5.1701 | 144.9294 | 5.1701 | 144.9294
[17 empty] | Marzo-Agosto | 0.047034 | 0.092962 | 21.4005 | 11.9867 | 9.4137 | 0.045928 | 204.9675 | 2.3462 | 204.9675 | 2.3462 | 204.9675
[17 empty] | Marzo-Septiembre | 0.047034 | 0.066553 | 13.8856 | 11.9867 | 1.8989 | 0.019519 | 97.284 | 7.4111 | 97.284 | 7.4111 | 97.284
[17 empty] | Marzo-Octubre | 0.047034 | 0.03196 | 11.3024 | 11.9867 | -0.6843 | -0.015074 | 45.3962 | 9.8516 | 45.3962 | 9.8516 | 45.3962
[17 empty] | Marzo-Noviembre | 0.047034 | 0.028267 | 8.0037 | 11.9867 | -3.983 | -0.018767 | 212.2368 | 2.0043 | 212.2368 | 2.0043 | 212.2368
[17 empty] | Marzo-Diciembre | 0.047034 | 0.018708 | 7.4421 | 11.9867 | -4.5446 | -0.028326 | 160.441 | 4.4405 | 160.441 | 4.4405 | 160.441
[17 empty] | Abril-Mayo | 0.1499 | 0.15334 | 29.0853 | 18.3946 | 10.6907 | 0.0034312 | 3115.7503 | -448.6697 | 0 | 0 |  | 54.0958 | 26.3078 | 10.2854 | fallo
[17 empty] | Abril-Junio | 0.1499 | 0.22834 | 36.1097 | 18.3946 | 17.7151 | 0.078435 | 225.8586 | -15.4626 | 225.8586 | 0 | 225.8586
[17 empty] | Abril-Julio | 0.1499 | 0.18446 | 31.904 | 18.3946 | 13.5095 | 0.034558 | 390.9263 | -40.207 | 390.9263 | 0 | 390.9263
[17 empty] | Abril-Agosto | 0.1499 | 0.092962 | 21.4005 | 18.3946 | 3.0059 | -0.056942 | -52.7886 | 26.3078 | 0 | 26.3078
[17 empty] | Abril-Septiembre | 0.1499 | 0.066553 | 13.8856 | 18.3946 | -4.5089 | -0.083351 | 54.0958 | 10.2854 | 54.0958 | 10.2854 | 54.0958
[17 empty] | Abril-Octubre | 0.1499 | 0.03196 | 11.3024 | 18.3946 | -7.0921 | -0.11794 | 60.1314 | 9.3806 | 60.1314 | 9.3806 | 60.1314
[17 empty] | Abril-Noviembre | 0.1499 | 0.028267 | 8.0037 | 18.3946 | -10.3909 | -0.12164 | 85.4253 | 5.589 | 85.4253 | 5.589 | 85.4253
[17 empty] | Abril-Diciembre | 0.1499 | 0.018708 | 7.4421 | 18.3946 | -10.9525 | -0.1312 | 83.4818 | 5.8803 | 83.4818 | 5.8803 | 83.4818
[17 empty] | Mayo-Junio | 0.15334 | 0.22834 | 36.1097 | 29.0853 | 7.0244 | 0.075003 | 93.6545 | 14.7247 | 93.6545 | 14.7247 | 93.6545 | 90.5576 | 15.1996 | 15.1996 | ok | 90.5576 | 15.1996 | 103861.2601 | 90.5576 | 15.1996
[17 empty] | Mayo-Julio | 0.15334 | 0.18446 | 31.904 | 29.0853 | 2.8187 | 0.031126 | 90.5576 | 15.1996 | 90.5576 | 15.1996 | 90.5576
[17 empty] | Mayo-Agosto | 0.15334 | 0.092962 | 21.4005 | 29.0853 | -7.6848 | -0.060373 | 127.2885 | 9.5674 | 127.2885 | 9.5674 | 127.2885
[17 empty] | Mayo-Septiembre | 0.15334 | 0.066553 | 13.8856 | 29.0853 | -15.1997 | -0.086782 | 175.1474 | 2.229 | 175.1474 | 2.229 | 175.1474
[17 empty] | Mayo-Octubre | 0.15334 | 0.03196 | 11.3024 | 29.0853 | -17.7829 | -0.12138 | 146.5116 | 6.6199 | 146.5116 | 6.6199 | 146.5116
[17 empty] | Mayo-Noviembre | 0.15334 | 0.028267 | 8.0037 | 29.0853 | -21.0816 | -0.12507 | 168.5609 | 3.2389 | 168.5609 | 3.2389 | 168.5609
[17 empty] | Mayo-Diciembre | 0.15334 | 0.018708 | 7.4421 | 29.0853 | -21.6432 | -0.13463 | 160.764 | 4.4345 | 160.764 | 4.4345 | 160.764
[17 empty] | Junio-Julio | 0.22834 | 0.18446 | 31.904 | 36.1097 | -4.2057 | -0.043877 | 95.8514 | 14.2231 | 95.8514 | 14.2231 | 95.8514 | 95.8514 | 14.2231 | 14.2231 | ok | 95.8514 | 14.2231 | 101633.3333 | 95.8514 | 14.2231
[17 empty] | Junio-Agosto | 0.22834 | 0.092962 | 21.4005 | 36.1097 | -14.7092 | -0.13538 | 108.6541 | 11.2997 | 108.6541 | 11.2997 | 108.6541
[17 empty] | Junio-Septiembre | 0.22834 | 0.066553 | 13.8856 | 36.1097 | -22.2241 | -0.16179 | 137.3675 | 4.7434 | 137.3675 | 4.7434 | 137.3675
[17 empty] | Junio-Octubre | 0.22834 | 0.03196 | 11.3024 | 36.1097 | -24.8073 | -0.19638 | 126.3237 | 7.2651 | 126.3237 | 7.2651 | 126.3237
[17 empty] | Junio-Noviembre | 0.22834 | 0.028267 | 8.0037 | 36.1097 | -28.106 | -0.20007 | 140.4798 | 4.0327 | 140.4798 | 4.0327 | 140.4798
[17 empty] | Junio-Diciembre | 0.22834 | 0.018708 | 7.4421 | 36.1097 | -28.6676 | -0.20963 | 136.753 | 4.8837 | 136.753 | 4.8837 | 136.753
[17 empty] | Julio-Agosto | 0.18446 | 0.092962 | 21.4005 | 31.904 | -10.5036 | -0.0915 | 114.7934 | 10.729 | 114.7934 | 10.729 | 114.7934 | 114.7934 | 10.729 | 10.729 | ok | 114.7934 | 10.729 | 93661.509 | 114.7934 | 10.729
[17 empty] | Julio-Septiembre | 0.18446 | 0.066553 | 13.8856 | 31.904 | -18.0184 | -0.11791 | 152.8168 | 3.7152 | 152.8168 | 3.7152 | 152.8168
[17 empty] | Julio-Octubre | 0.18446 | 0.03196 | 11.3024 | 31.904 | -20.6016 | -0.1525 | 135.0911 | 6.9849 | 135.0911 | 6.9849 | 135.0911
[17 empty] | Julio-Noviembre | 0.18446 | 0.028267 | 8.0037 | 31.904 | -23.9003 | -0.15619 | 153.0164 | 3.6783 | 153.0164 | 3.6783 | 153.0164
[17 empty] | Julio-Diciembre | 0.18446 | 0.018708 | 7.4421 | 31.904 | -24.4619 | -0.16575 | 147.5802 | 4.6811 | 147.5802 | 4.6811 | 147.5802
[17 empty] | Agosto-Septiembre | 0.092962 | 0.066553 | 13.8856 | 21.4005 | -7.5148 | -0.026409 | 284.5579 | -5.0526 | 284.5579 | 0 | 284.5579 | 165.5365 | 6.0118 | 6.0118 | ok | 165.5365 | 6.0118 | 92967.2652 | 165.5365 | 6.0118
[17 empty] | Agosto-Octubre | 0.092962 | 0.03196 | 11.3024 | 21.4005 | -10.098 | -0.061002 | 165.5365 | 6.0118 | 165.5365 | 6.0118 | 165.5365
[17 empty] | Agosto-Noviembre | 0.092962 | 0.028267 | 8.0037 | 21.4005 | -13.3968 | -0.064695 | 207.0762 | 2.1502 | 207.0762 | 2.1502 | 207.0762
[17 empty] | Agosto-Diciembre | 0.092962 | 0.018708 | 7.4421 | 21.4005 | -13.9584 | -0.074254 | 187.9818 | 3.9253 | 187.9818 | 3.9253 | 187.9818
[17 empty] | Septiembre-Octubre | 0.066553 | 0.03196 | 11.3024 | 13.8856 | -2.5832 | -0.034593 | 74.6739 | 8.9158 | 74.6739 | 8.9158 | 74.6739 | 74.6739 | 8.9158 | 8.9158 | ok | 74.6739 | 8.9158 | 69545.0175 | 74.6739 | 8.9158
[17 empty] | Septiembre-Noviembre | 0.066553 | 0.028267 | 8.0037 | 13.8856 | -5.8819 | -0.038286 | 153.6313 | 3.661 | 153.6313 | 3.661 | 153.6313
[17 empty] | Septiembre-Diciembre | 0.066553 | 0.018708 | 7.4421 | 13.8856 | -6.4435 | -0.047845 | 134.6752 | 4.9225 | 134.6752 | 4.9225 | 134.6752
[17 empty] | Octubre-Noviembre | 0.03196 | 0.028267 | 8.0037 | 11.3024 | -3.2987 | -0.0036931 | 893.2233 | -17.2453 | 0 | 0 |  | 291.3019 | 1.9923 | 1.9923 | ok | 291.3019 | 1.9923 | 125386.6391 | 291.3019 | 1.9923
[17 empty] | Octubre-Diciembre | 0.03196 | 0.018708 | 7.4421 | 11.3024 | -3.8603 | -0.013252 | 291.3019 | 1.9923 | 291.3019 | 1.9923 | 291.3019
[17 empty] | Noviembre-Diciembre | 0.028267 | 0.018708 | 7.4421 | 8.0037 | -0.5616 | -0.009559 | 58.751 | 6.343 | 58.751 | 6.343 | 58.751 | 58.751 | 6.343 | 6.343 | ok | 58.751 | 6.343 | 51726.5868 | 58.751 | 6.343
[16 empty] | 19 | 5.4182
5.2241
3.7864
2.4674
1.5605
1.2569
1.4226
2.1208
3.2686
4.0156
5.6707
6.0986
Note on M19: waliki: Si #¡NUM! Significa que no hay más opciones.

## Radiation
| 30 | HORIZONTAL RADIATION kWh/m2/month | [11 empty] | LATITUD [ º ]
|  | January | February | March | April | May | June | July | August | Sept. | Oct. | Nov. | Dec.
1 | POLAND | 183 | 156 | 126 | 84 | 57 | 45 | 54 | 78 | 108 | 135 | 168 | 183 | -33
2 | SPAIN | 210.8 | 162.4 | 142.6 | 93 | 58.9 | 42 | 49.6 | 77.5 | 117 | 158.1 | 186 | 210.8 | -36.8
3 | UCRANIA | 177 | 165.2 | 162 | 132 | 102 | 84 | 81 | 102 | 123 | 153 | 171 | 201 | -18.5
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
| RAD | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453
| Incl | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
| Incli Rad | 0.33161 | 0.33161 | 0.33161 | 0.33161 | 0.33161 | 0.33161 | 0.33161 | 0.33161 | 0.33161 | 0.33161 | 0.33161 | 0.33161
| Sen Incli | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557 | 0.32557
| Cos Incli | 0.94552 | 0.94552 | 0.94552 | 0.94552 | 0.94552 | 0.94552 | 0.94552 | 0.94552 | 0.94552 | 0.94552 | 0.94552 | 0.94552
| Lat | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33
| Lat. Rad | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596
| SLT | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464
| CLT | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867
| TLT | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941
| LT Incli Rad | -0.90757 | -0.90757 | -0.90757 | -0.90757 | -0.90757 | -0.90757 | -0.90757 | -0.90757 | -0.90757 | -0.90757 | -0.90757 | -0.90757
| SLTINCL | -0.78801 | -0.78801 | -0.78801 | -0.78801 | -0.78801 | -0.78801 | -0.78801 | -0.78801 | -0.78801 | -0.78801 | -0.78801 | -0.78801
| CLTINCL | 0.61566 | 0.61566 | 0.61566 | 0.61566 | 0.61566 | 0.61566 | 0.61566 | 0.61566 | 0.61566 | 0.61566 | 0.61566 | 0.61566
| TLTINCL | -1.2799 | -1.2799 | -1.2799 | -1.2799 | -1.2799 | -1.2799 | -1.2799 | -1.2799 | -1.2799 | -1.2799 | -1.2799 | -1.2799
| Cos 37.5 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335
| Rad 23.45 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928
| N | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
| IOEXT | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8
| PI.24IOEXT | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171
| N | 15 | 46 | 74 | 105 | 135 | 166 | 196 | 227 | 258 | 270 | 319 | 349
| Rad 360 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214
| D.Rad | -0.37122 | -0.23194 | -0.049199 | 0.16432 | 0.32798 | 0.40691 | 0.37555 | 0.24057 | 0.038692 | -0.0457 | -0.33419 | -0.40728
| SDE | -0.36275 | -0.22987 | -0.049179 | 0.16358 | 0.32213 | 0.39578 | 0.36678 | 0.23825 | 0.038682 | -0.045684 | -0.32801 | -0.39611
| CDE | 0.93188 | 0.97322 | 0.99879 | 0.98653 | 0.94669 | 0.91835 | 0.93031 | 0.9712 | 0.99925 | 0.99896 | 0.94468 | 0.9182
| W1 | -0.25279 | -0.15338 | -0.031976 | 0.10768 | 0.22097 | 0.27987 | 0.25604 | 0.15931 | 0.025139 | -0.029698 | -0.22548 | -0.28015
| W1 | -75.357 | -81.1769 | -88.1676 | 83.8183 | 77.2337 | 73.7474 | 75.1651 | 80.833 | 88.5595 | -88.2982 | -76.9686 | -73.7307
| W1 | 104.643 | 98.8231 | 91.8324 | 83.8183 | 77.2337 | 73.7474 | 75.1651 | 80.833 | 88.5595 | 91.7018 | 103.0314 | 106.2693
| W1.Rad | 1.8264 | 1.7248 | 1.6028 | 1.4629 | 1.348 | 1.2871 | 1.3119 | 1.4108 | 1.5457 | 1.6005 | 1.7982 | 1.8547
| W2 | 0.49824 | 0.30231 | -0.063022 | 0.21223 | 0.43553 | 0.55161 | 0.50463 | 0.31399 | 0.049548 | -0.058534 | -0.44442 | -0.55216
| W2 | 65.9653 | 73.8609 | -86.401 | 78.2714 | 68.2332 | 64.2194 | 65.7476 | 73.3232 | 87.1669 | -86.6558 | -67.8971 | -64.2022
| W2 | 65.9653 | 73.8609 | 93.599 | 78.2714 | 68.2332 | 64.2194 | 65.7476 | 73.3232 | 87.1669 | 93.3442 | 112.1029 | 115.7978
| W2.RAD | 1.1513 | 1.2891 | 1.6336 | 1.3661 | 1.1909 | 1.1208 | 1.1475 | 1.2797 | 1.5213 | 1.6292 | 1.9566 | 2.0211
| H0 | 1.117 | 1.0225 | 0.88016 | 0.69223 | 0.53784 | 0.46196 | 0.49215 | 0.62105 | 0.80521 | 0.87725 | 1.0931 | 1.1394
| H0 | 42889.7059 | 38928.9794 | 33067.0427 | 25558.5801 | 19561.4358 | 16645.1794 | 17724.8243 | 22559.66 | 29697.3609 | 32573.0506 | 41617.9479 | 43742.5245
| Radiación | 15739.83 | 13417.56 | 10837.26 | 7224.84 | 4902.57 | 3870.45 | 4644.54 | 6708.78 | 9289.08 | 11611.35 | 14449.68 | 15739.83
| K1 | 0.36698 | 0.34467 | 0.32774 | 0.28268 | 0.25062 | 0.23253 | 0.26204 | 0.29738 | 0.31279 | 0.35647 | 0.3472 | 0.35983
| K(I) | 0.36698 | 0.34467 | 0.32774 | 0.28268 | 0.25062 | 0.23253 | 0.26204 | 0.29738 | 0.31279 | 0.35647 | 0.3472 | 0.35983
| H1 | 0.50211 | 0.53059 | 0.55373 | 0.62244 | 0.67838 | 0.71282 | 0.65775 | 0.59882 | 0.57532 | 0.51525 | 0.52725 | 0.511
| R | 1.117 | 1.0225 | 0.88016 | 0.69223 | 0.53784 | 0.46196 | 0.49215 | 0.62105 | 0.80521 | 0.87725 | 1.0931 | 1.1394
| R | 0.76374 | 0.79127 | 0.76886 | 0.6047 | 0.44434 | 0.34538 | 0.38716 | 0.53541 | 0.7055 | 0.76645 | 0.94356 | 0.98441
| H | 0.87414 | 0.89302 | 0.88721 | 0.83925 | 0.80826 | 0.79803 | 0.77778 | 0.80275 | 0.86471 | 0.8782 | 0.9644 | 0.9839
| OM | 0.18681 | 0.11837 | 0.025325 | -0.084239 | -0.16589 | -0.20381 | -0.18888 | -0.12269 | -0.01992 | 0.023526 | 0.16891 | 0.20398
| OM | 0.28585 | 0.18114 | 0.038753 | -0.1289 | -0.25384 | -0.31188 | -0.28903 | -0.18775 | -0.030482 | 0.035999 | 0.25847 | 0.31214
| OM | 0.87211 | 0.7934 | 0.6671 | 0.49173 | 0.34173 | 0.26587 | 0.29624 | 0.42325 | 0.59816 | 0.66445 | 0.85278 | 0.88979
| OM | 0.74102 | 0.65649 | 0.5266 | 0.35295 | 0.20856 | 0.13668 | 0.16537 | 0.28662 | 0.45759 | 0.52393 | 0.71989 | 0.76062
| OM | 42.1815 | 48.9669 | 58.224 | 69.332 | 77.9622 | 82.1443 | 80.4814 | 73.3441 | 62.7683 | 58.404 | 43.9548 | 40.4808
|  | 14446.7114 | 12581.2089 | 10095.6868 | 6366.5855 | 4160.6692 | 3243.1891 | 3793.073 | 5654.7506 | 8433.9416 | 10706.9224 | 14632.0763 | 16260.7904 | 1283.2881
| RAD | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453
| Incl | 26.47 | 26.47 | 26.47 | 26.47 | 26.47 | 26.47 | 26.47 | 26.47 | 26.47 | 26.47 | 26.47 | 26.47
| Incli Rad | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199
| Sen Incli | 0.44573 | 0.44573 | 0.44573 | 0.44573 | 0.44573 | 0.44573 | 0.44573 | 0.44573 | 0.44573 | 0.44573 | 0.44573 | 0.44573
| Cos Incli | 0.89517 | 0.89517 | 0.89517 | 0.89517 | 0.89517 | 0.89517 | 0.89517 | 0.89517 | 0.89517 | 0.89517 | 0.89517 | 0.89517
| Lat | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33
| Lat. Rad | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596
| SLT | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464
| CLT | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867
| TLT | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941
| LT Incli Rad | -1.0379 | -1.0379 | -1.0379 | -1.0379 | -1.0379 | -1.0379 | -1.0379 | -1.0379 | -1.0379 | -1.0379 | -1.0379 | -1.0379
| SLTINCL | -0.86136 | -0.86136 | -0.86136 | -0.86136 | -0.86136 | -0.86136 | -0.86136 | -0.86136 | -0.86136 | -0.86136 | -0.86136 | -0.86136
| CLTINCL | 0.50799 | 0.50799 | 0.50799 | 0.50799 | 0.50799 | 0.50799 | 0.50799 | 0.50799 | 0.50799 | 0.50799 | 0.50799 | 0.50799
| TLTINCL | -1.6956 | -1.6956 | -1.6956 | -1.6956 | -1.6956 | -1.6956 | -1.6956 | -1.6956 | -1.6956 | -1.6956 | -1.6956 | -1.6956
| Cos 37.5 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335
| Rad 23.45 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928
| N | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
| IOEXT | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8
| PI.24IOEXT | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171
| N | 15 | 46 | 74 | 105 | 135 | 166 | 196 | 227 | 258 | 270 | 319 | 349
| Rad 360 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214
| D.Rad | -0.37122 | -0.23194 | -0.049199 | 0.16432 | 0.32798 | 0.40691 | 0.37555 | 0.24057 | 0.038692 | -0.0457 | -0.33419 | -0.40728
| SDE | -0.36275 | -0.22987 | -0.049179 | 0.16358 | 0.32213 | 0.39578 | 0.36678 | 0.23825 | 0.038682 | -0.045684 | -0.32801 | -0.39611
| CDE | 0.93188 | 0.97322 | 0.99879 | 0.98653 | 0.94669 | 0.91835 | 0.93031 | 0.9712 | 0.99925 | 0.99896 | 0.94468 | 0.9182
| W1 | -0.25279 | -0.15338 | -0.031976 | 0.10768 | 0.22097 | 0.27987 | 0.25604 | 0.15931 | 0.025139 | -0.029698 | -0.22548 | -0.28015
| W1 | -75.357 | -81.1769 | -88.1676 | 83.8183 | 77.2337 | 73.7474 | 75.1651 | 80.833 | 88.5595 | -88.2982 | -76.9686 | -73.7307
| W1 | 104.643 | 98.8231 | 91.8324 | 83.8183 | 77.2337 | 73.7474 | 75.1651 | 80.833 | 88.5595 | 91.7018 | 103.0314 | 106.2693
| W1.Rad | 1.8264 | 1.7248 | 1.6028 | 1.4629 | 1.348 | 1.2871 | 1.3119 | 1.4108 | 1.5457 | 1.6005 | 1.7982 | 1.8547
| W2 | -0.66006 | -0.40049 | -0.08349 | 0.28116 | 0.57697 | 0.73076 | 0.66852 | 0.41597 | 0.06564 | -0.077544 | -0.58875 | -0.73149
| W2 | -48.6956 | -66.3911 | -85.2108 | 73.6704 | 54.7621 | 43.0498 | 48.0471 | 65.4195 | 86.2364 | -85.5526 | -53.9316 | -42.9885
| W2 | 131.3044 | 113.6089 | 94.7892 | 73.6704 | 54.7621 | 43.0498 | 48.0471 | 65.4195 | 86.2364 | 94.4474 | 126.0684 | 137.0115
| W2.RAD | 2.2917 | 1.9828 | 1.6544 | 1.2858 | 0.95578 | 0.75136 | 0.83858 | 1.1418 | 1.5051 | 1.6484 | 2.2003 | 2.3913
| H0 | 1.117 | 1.0225 | 0.88016 | 0.69223 | 0.53784 | 0.46196 | 0.49215 | 0.62105 | 0.80521 | 0.87725 | 1.0931 | 1.1394
| H0 | 42889.7059 | 38928.9794 | 33067.0427 | 25558.5801 | 19561.4358 | 16645.1794 | 17724.8243 | 22559.66 | 29697.3609 | 32573.0506 | 41617.9479 | 43742.5245
| Radiación | 15739.83 | 13417.56 | 10837.26 | 7224.84 | 4902.57 | 3870.45 | 4644.54 | 6708.78 | 9289.08 | 11611.35 | 14449.68 | 15739.83
| K1 | 0.36698 | 0.34467 | 0.32774 | 0.28268 | 0.25062 | 0.23253 | 0.26204 | 0.29738 | 0.31279 | 0.35647 | 0.3472 | 0.35983
| K(I) | 0.36698 | 0.34467 | 0.32774 | 0.28268 | 0.25062 | 0.23253 | 0.26204 | 0.29738 | 0.31279 | 0.35647 | 0.3472 | 0.35983
| H1 | 0.50211 | 0.53059 | 0.55373 | 0.62244 | 0.67838 | 0.71282 | 0.65775 | 0.59882 | 0.57532 | 0.51525 | 0.52725 | 0.511
| R | 1.117 | 1.0225 | 0.88016 | 0.69223 | 0.53784 | 0.46196 | 0.49215 | 0.62105 | 0.80521 | 0.87725 | 1.0931 | 1.1394
| R | 0.92094 | 0.81179 | 0.6533 | 0.43303 | 0.23722 | 0.13488 | 0.17581 | 0.34511 | 0.56676 | 0.65001 | 0.89248 | 0.94841
| H | 0.9448 | 0.89432 | 0.82674 | 0.7638 | 0.7296 | 0.72467 | 0.69392 | 0.71636 | 0.79634 | 0.81382 | 0.93202 | 0.95847
| OM | 0.17686 | 0.11207 | 0.023977 | -0.079754 | -0.15705 | -0.19296 | -0.17882 | -0.11616 | -0.018859 | 0.022273 | 0.15992 | 0.19312
| OM | 0.31246 | 0.198 | 0.042361 | -0.1409 | -0.27747 | -0.34091 | -0.31593 | -0.20522 | -0.03332 | 0.03935 | 0.28253 | 0.34119
| OM | 0.8675 | 0.77766 | 0.63725 | 0.44668 | 0.28639 | 0.20607 | 0.23817 | 0.37323 | 0.56185 | 0.63434 | 0.84519 | 0.88809
| OM | 0.68803 | 0.59022 | 0.44489 | 0.25668 | 0.10406 | 0.0292 | 0.058994 | 0.18619 | 0.36939 | 0.44194 | 0.66325 | 0.71124
| OM | 46.5258 | 53.8273 | 63.5838 | 75.1267 | 84.027 | 88.3267 | 86.6179 | 79.2698 | 68.3218 | 63.772 | 48.4517 | 44.6638
|  | 15614.5556 | 12599.6041 | 9407.5518 | 5794.2178 | 3755.7602 | 2945.0528 | 3384.1043 | 5046.223 | 7767.1337 | 9921.9857 | 14140.7416 | 15840.4735 | 1234.9425
| RAD | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453
| Incl | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
| Incli Rad | 0.31416 | 0.31416 | 0.31416 | 0.31416 | 0.31416 | 0.31416 | 0.31416 | 0.31416 | 0.31416 | 0.31416 | 0.31416 | 0.31416
| Sen Incli | 0.30902 | 0.30902 | 0.30902 | 0.30902 | 0.30902 | 0.30902 | 0.30902 | 0.30902 | 0.30902 | 0.30902 | 0.30902 | 0.30902
| Cos Incli | 0.95106 | 0.95106 | 0.95106 | 0.95106 | 0.95106 | 0.95106 | 0.95106 | 0.95106 | 0.95106 | 0.95106 | 0.95106 | 0.95106
| Lat | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33
| Lat. Rad | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596
| SLT | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464
| CLT | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867
| TLT | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941
| LT Incli Rad | -0.89012 | -0.89012 | -0.89012 | -0.89012 | -0.89012 | -0.89012 | -0.89012 | -0.89012 | -0.89012 | -0.89012 | -0.89012 | -0.89012
| SLTINCL | -0.77715 | -0.77715 | -0.77715 | -0.77715 | -0.77715 | -0.77715 | -0.77715 | -0.77715 | -0.77715 | -0.77715 | -0.77715 | -0.77715
| CLTINCL | 0.62932 | 0.62932 | 0.62932 | 0.62932 | 0.62932 | 0.62932 | 0.62932 | 0.62932 | 0.62932 | 0.62932 | 0.62932 | 0.62932
| TLTINCL | -1.2349 | -1.2349 | -1.2349 | -1.2349 | -1.2349 | -1.2349 | -1.2349 | -1.2349 | -1.2349 | -1.2349 | -1.2349 | -1.2349
| Cos 37.5 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335
| Rad 23.45 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928
| N | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
| IOEXT | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8
| PI.24IOEXT | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171
| N | 15 | 46 | 74 | 105 | 135 | 166 | 196 | 227 | 258 | 270 | 319 | 349
| Rad 360 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214
| D.Rad | -0.37122 | -0.23194 | -0.049199 | 0.16432 | 0.32798 | 0.40691 | 0.37555 | 0.24057 | 0.038692 | -0.0457 | -0.33419 | -0.40728
| SDE | -0.36275 | -0.22987 | -0.049179 | 0.16358 | 0.32213 | 0.39578 | 0.36678 | 0.23825 | 0.038682 | -0.045684 | -0.32801 | -0.39611
| CDE | 0.93188 | 0.97322 | 0.99879 | 0.98653 | 0.94669 | 0.91835 | 0.93031 | 0.9712 | 0.99925 | 0.99896 | 0.94468 | 0.9182
| W1 | -0.25279 | -0.15338 | -0.031976 | 0.10768 | 0.22097 | 0.27987 | 0.25604 | 0.15931 | 0.025139 | -0.029698 | -0.22548 | -0.28015
| W1 | -75.357 | -81.1769 | -88.1676 | 83.8183 | 77.2337 | 73.7474 | 75.1651 | 80.833 | 88.5595 | -88.2982 | -76.9686 | -73.7307
| W1 | 104.643 | 98.8231 | 91.8324 | 83.8183 | 77.2337 | 73.7474 | 75.1651 | 80.833 | 88.5595 | 91.7018 | 103.0314 | 106.2693
| W1.Rad | 1.8264 | 1.7248 | 1.6028 | 1.4629 | 1.348 | 1.2871 | 1.3119 | 1.4108 | 1.5457 | 1.6005 | 1.7982 | 1.8547
| W2 | -0.48071 | -0.29167 | -0.060804 | 0.20477 | 0.4202 | 0.5322 | 0.48687 | 0.30294 | 0.047804 | -0.056474 | -0.42878 | -0.53273
| W2 | -61.2683 | -73.042 | -86.514 | 78.1842 | 65.1529 | 57.8458 | 60.8649 | 72.3655 | 87.26 | -86.7626 | -64.6101 | -57.8098
| W2 | 118.7317 | 106.958 | 93.486 | 78.1842 | 65.1529 | 57.8458 | 60.8649 | 72.3655 | 87.26 | 93.2374 | 115.3899 | 122.1902
| W2.RAD | 2.0723 | 1.8668 | 1.6316 | 1.3646 | 1.1371 | 1.0096 | 1.0623 | 1.263 | 1.523 | 1.6273 | 2.0139 | 2.1326
| H0 | 1.117 | 1.0225 | 0.88016 | 0.69223 | 0.53784 | 0.46196 | 0.49215 | 0.62105 | 0.80521 | 0.87725 | 1.0931 | 1.1394
| H0 | 42889.7059 | 38928.9794 | 33067.0427 | 25558.5801 | 19561.4358 | 16645.1794 | 17724.8243 | 22559.66 | 29697.3609 | 32573.0506 | 41617.9479 | 43742.5245
| Radiación | 15739.83 | 13417.56 | 10837.26 | 7224.84 | 4902.57 | 3870.45 | 4644.54 | 6708.78 | 9289.08 | 11611.35 | 14449.68 | 15739.83
| K1 | 0.36698 | 0.34467 | 0.32774 | 0.28268 | 0.25062 | 0.23253 | 0.26204 | 0.29738 | 0.31279 | 0.35647 | 0.3472 | 0.35983
| K(I) | 0.36698 | 0.34467 | 0.32774 | 0.28268 | 0.25062 | 0.23253 | 0.26204 | 0.29738 | 0.31279 | 0.35647 | 0.3472 | 0.35983
| H1 | 0.50211 | 0.53059 | 0.55373 | 0.62244 | 0.67838 | 0.71282 | 0.65775 | 0.59882 | 0.57532 | 0.51525 | 0.52725 | 0.511
| R | 1.117 | 1.0225 | 0.88016 | 0.69223 | 0.53784 | 0.46196 | 0.49215 | 0.62105 | 0.80521 | 0.87725 | 1.0931 | 1.1394
| R | 0.96892 | 0.89325 | 0.78338 | 0.62727 | 0.47589 | 0.38696 | 0.42383 | 0.56134 | 0.72322 | 0.78109 | 0.9492 | 0.98797
| H | 0.97713 | 0.9418 | 0.89467 | 0.84894 | 0.81973 | 0.8114 | 0.7916 | 0.81426 | 0.87327 | 0.88617 | 0.96797 | 0.98651
| OM | 0.1879 | 0.11907 | 0.025474 | -0.084733 | -0.16686 | -0.20501 | -0.18999 | -0.12341 | -0.020037 | 0.023663 | 0.1699 | 0.20518
| OM | 0.28191 | 0.17864 | 0.038219 | -0.12713 | -0.25034 | -0.30758 | -0.28504 | -0.18516 | -0.030062 | 0.035503 | 0.25491 | 0.30784
| OM | 0.87161 | 0.79449 | 0.67025 | 0.49715 | 0.34872 | 0.27355 | 0.30365 | 0.42942 | 0.60226 | 0.66764 | 0.8527 | 0.88887
| OM | 0.74718 | 0.66454 | 0.53689 | 0.36542 | 0.22232 | 0.15093 | 0.17943 | 0.29974 | 0.46884 | 0.53426 | 0.72656 | 0.76627
| OM | 41.6534 | 48.3527 | 57.5279 | 68.5665 | 77.1549 | 81.3192 | 79.6632 | 72.5582 | 62.0411 | 57.7066 | 43.4012 | 39.9799
|  | 16148.9196 | 13268.491 | 10180.5626 | 6440.0979 | 4219.7089 | 3297.4906 | 3860.4481 | 5735.7999 | 8517.4959 | 10804.0964 | 14686.2609 | 16303.8007 | 1319.1858
| RAD | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453 | 0.017453
| Incl | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
| Incli Rad | 0.22689 | 0.22689 | 0.22689 | 0.22689 | 0.22689 | 0.22689 | 0.22689 | 0.22689 | 0.22689 | 0.22689 | 0.22689 | 0.22689
| Sen Incli | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 0.22495
| Cos Incli | 0.97437 | 0.97437 | 0.97437 | 0.97437 | 0.97437 | 0.97437 | 0.97437 | 0.97437 | 0.97437 | 0.97437 | 0.97437 | 0.97437
| Lat | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33 | -33
| Lat. Rad | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596 | -0.57596
| SLT | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464 | -0.54464
| CLT | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867 | 0.83867
| TLT | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941 | -0.64941
| LT Incli Rad | -0.80285 | -0.80285 | -0.80285 | -0.80285 | -0.80285 | -0.80285 | -0.80285 | -0.80285 | -0.80285 | -0.80285 | -0.80285 | -0.80285
| SLTINCL | -0.71934 | -0.71934 | -0.71934 | -0.71934 | -0.71934 | -0.71934 | -0.71934 | -0.71934 | -0.71934 | -0.71934 | -0.71934 | -0.71934
| CLTINCL | 0.69466 | 0.69466 | 0.69466 | 0.69466 | 0.69466 | 0.69466 | 0.69466 | 0.69466 | 0.69466 | 0.69466 | 0.69466 | 0.69466
| TLTINCL | -1.0355 | -1.0355 | -1.0355 | -1.0355 | -1.0355 | -1.0355 | -1.0355 | -1.0355 | -1.0355 | -1.0355 | -1.0355 | -1.0355
| Cos 37.5 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335 | 0.79335
| Rad 23.45 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928 | 0.40928
| N | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
| IOEXT | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8 | 4870.8
| PI.24IOEXT | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171 | 37210.171
| N | 15 | 46 | 74 | 105 | 135 | 166 | 196 | 227 | 258 | 270 | 319 | 349
| Rad 360 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214 | 0.017214
| D.Rad | -0.37122 | -0.23194 | -0.049199 | 0.16432 | 0.32798 | 0.40691 | 0.37555 | 0.24057 | 0.038692 | -0.0457 | -0.33419 | -0.40728
| SDE | -0.36275 | -0.22987 | -0.049179 | 0.16358 | 0.32213 | 0.39578 | 0.36678 | 0.23825 | 0.038682 | -0.045684 | -0.32801 | -0.39611
| CDE | 0.93188 | 0.97322 | 0.99879 | 0.98653 | 0.94669 | 0.91835 | 0.93031 | 0.9712 | 0.99925 | 0.99896 | 0.94468 | 0.9182
| W1 | -0.25279 | -0.15338 | -0.031976 | 0.10768 | 0.22097 | 0.27987 | 0.25604 | 0.15931 | 0.025139 | -0.029698 | -0.22548 | -0.28015
| W1 | -75.357 | -81.1769 | -88.1676 | 83.8183 | 77.2337 | 73.7474 | 75.1651 | 80.833 | 88.5595 | -88.2982 | -76.9686 | -73.7307
| W1 | 104.643 | 98.8231 | 91.8324 | 83.8183 | 77.2337 | 73.7474 | 75.1651 | 80.833 | 88.5595 | 91.7018 | 103.0314 | 106.2693
| W1.Rad | 1.8264 | 1.7248 | 1.6028 | 1.4629 | 1.348 | 1.2871 | 1.3119 | 1.4108 | 1.5457 | 1.6005 | 1.7982 | 1.8547
| W2 | -0.4031 | -0.24458 | -0.050988 | 0.17171 | 0.35236 | 0.44628 | 0.40827 | 0.25404 | 0.040087 | -0.047356 | -0.35955 | -0.44672
| W2 | -66.2278 | -75.8429 | -87.0773 | 80.1129 | 69.3683 | 63.4948 | 65.9039 | 75.2835 | 87.7026 | -87.2857 | -68.9273 | -63.4663
| W2 | 113.7722 | 104.1571 | 92.9227 | 80.1129 | 69.3683 | 63.4948 | 65.9039 | 75.2835 | 87.7026 | 92.7143 | 111.0727 | 116.5337
| W2.RAD | 1.9857 | 1.8179 | 1.6218 | 1.3982 | 1.2107 | 1.1082 | 1.1502 | 1.3139 | 1.5307 | 1.6182 | 1.9386 | 2.0339
| H0 | 1.117 | 1.0225 | 0.88016 | 0.69223 | 0.53784 | 0.46196 | 0.49215 | 0.62105 | 0.80521 | 0.87725 | 1.0931 | 1.1394
| H0 | 42889.7059 | 38928.9794 | 33067.0427 | 25558.5801 | 19561.4358 | 16645.1794 | 17724.8243 | 22559.66 | 29697.3609 | 32573.0506 | 41617.9479 | 43742.5245
| Radiación | 15739.83 | 13417.56 | 10837.26 | 7224.84 | 4902.57 | 3870.45 | 4644.54 | 6708.78 | 9289.08 | 11611.35 | 14449.68 | 15739.83
| K1 | 0.36698 | 0.34467 | 0.32774 | 0.28268 | 0.25062 | 0.23253 | 0.26204 | 0.29738 | 0.31279 | 0.35647 | 0.3472 | 0.35983
| K(I) | 0.36698 | 0.34467 | 0.32774 | 0.28268 | 0.25062 | 0.23253 | 0.26204 | 0.29738 | 0.31279 | 0.35647 | 0.3472 | 0.35983
| H1 | 0.50211 | 0.53059 | 0.55373 | 0.62244 | 0.67838 | 0.71282 | 0.65775 | 0.59882 | 0.57532 | 0.51525 | 0.52725 | 0.511
| R | 1.117 | 1.0225 | 0.88016 | 0.69223 | 0.53784 | 0.46196 | 0.49215 | 0.62105 | 0.80521 | 0.87725 | 1.0931 | 1.1394
| R | 0.98738 | 0.93229 | 0.85231 | 0.73761 | 0.62268 | 0.55283 | 0.58204 | 0.68808 | 0.80847 | 0.85064 | 0.97302 | 1.0012
| H | 0.98984 | 0.96398 | 0.92956 | 0.89552 | 0.87252 | 0.86501 | 0.85109 | 0.86975 | 0.91385 | 0.92356 | 0.98305 | 0.99662
| OM | 0.19251 | 0.12199 | 0.026098 | -0.08681 | -0.17095 | -0.21003 | -0.19464 | -0.12644 | -0.020528 | 0.024244 | 0.17407 | 0.21021
| OM | 0.26094 | 0.16535 | 0.035376 | -0.11767 | -0.23172 | -0.2847 | -0.26384 | -0.17139 | -0.027826 | 0.032862 | 0.23595 | 0.28494
| OM | 0.86509 | 0.7963 | 0.6829 | 0.5219 | 0.38203 | 0.31067 | 0.33928 | 0.45825 | 0.62 | 0.68049 | 0.84839 | 0.88022
| OM | 0.77451 | 0.7017 | 0.58582 | 0.42601 | 0.29001 | 0.22141 | 0.24886 | 0.36385 | 0.52287 | 0.5834 | 0.75657 | 0.79097
| OM | 39.239 | 45.4362 | 54.1391 | 64.7851 | 73.1414 | 77.208 | 75.59 | 68.663 | 58.4749 | 54.3102 | 40.8375 | 37.7239
|  | 16358.9624 | 13580.9613 | 10577.5218 | 6793.4735 | 4491.4538 | 3515.3689 | 4150.5512 | 6126.7212 | 8913.2631 | 11259.9519 | 14914.9879 | 16470.9744 | 1362.0997
Temperaturas medias mensuales/anuales ºC 1.971-2000
|  | Enero | Febrero | Marzo | Abril | Mayo | Junio | Julio | Agosto | Sept. | Oct. | Nov. | Dic. | Máxima
| Valparaíso | 21 | 21 | 18.5 | 15 | 11.5 | 10 | 8.5 | 10 | 11.5 | 14.5 | 17.5 | 19.5 | 21
| Arica | 23 | 23 | 22.5 | 20.5 | 19 | 17.5 | 16.5 | 16.5 | 17 | 18.5 | 19.5 | 21 | 23
| Concepción | 17 | 16.5 | 15.5 | 13 | 12 | 10.5 | 9.5 | 10 | 10.5 | 12.5 | 14 | 15.5 | 17
| Punta Arenas | 11 | 11 | 8.5 | 7 | 4.5 | 2 | 1.5 | 3 | 4.5 | 4.5 | 7 | 9 | 11